2.19 CARBON MONOXIDE MONITOR

- Manufacturers:

- American Gas Safety (AGS) AGSCH4CO

- Approved Alternatives

- Description: Contractor is to provide one Carbon Monoxide (CO) monitor, interlocked with each boiler.

- The CO monitor shall protect the boiler equipment room to ensure that pre-determined levels of CO are not exceeded. The monitor shall provide a visual and audible alarm at 25 PPM. The monitor shall shut down the combustion process in the room when 50 PPM is reached.

- At 50 PPM the monitor shall indicate the Max PPM reached as well as the current PPM level in the room.

- The monitor shall be hard wired 110v powered.

- The monitor shall require manual re-set after an alarm condition.

- The monitor shall auto re-set after a power loss.

- The monitor shall provide dry contact SPDT Form C relay output.

- The monitor shall provide a 110v 3 amp output which de-energizes in alarm.

- The monitor shall be constructed of NEMA 1 polycarbonate plastic with a digital TFT screen. The monitor shall be mounted on a dual gang rough in handy box.

- Warranty:

- The manufacturer shall provide a 3 year limited warranty from date of install.