SECTION 23 8500 – EMERGENCY GAS SHUTDOWN SYSTEM

PART 1 - GENERAL

| 1.1 |  | RELATED DOCUMENTS |
| --- | --- | --- |
|  | A. | Drawings and general provisions of the Contract, including General and Supplementary General Conditions and other Division 01 Specification Sections, apply to this Section. |
| 1.2 |  | SUMMARY |
|  | A. | Provide a complete installation of an emergency boiler room gas shutdown system consisting of an emergency shunt switch located at each exit and normally closed gas solenoid valve. The emergency shunt switches shall provide control over the power supply to the gas solenoid valve. If the switches are activated, the gas solenoid valve will close and will require a manual re-set to open the gas solenoid valve per code. |

PART 2 - PRODUCTS

  - Emergency Shunt Switch Type American Gas Safety model# AGSEGOTW

    - Labeled “Emergency Gas Off”

    - When the emergency shunt switch enters alarm, it will in turn de-energize and close the gas solenoid valve.

    - Clear lift cover to prevent inadvertent shutdowns with a red mushroom twist release button for reset after emergency.

    - Outdoor weatherproof option AGSEGOTWWM.

  - Gas Solenoid Valve type AGS GSV

    - Provide a Gas Solenoid Valve: UL Listed 429, CSA certified, gas safety shut-off valve. Aluminum body two-way normally closed valve rated for natural gas (methane) and LPG (liquid petroleum gas). Size to be same as pipe size indicated on plans, 120 volt ac single phase actuator, 15 watts, and 5 PSI maximum operating pressure capacity.

    - Gas solenoid valve shall be placed to shut down the fuel supply to each boiler located inside the room.

PART 3 - EXECUTION

  - INSTALLATION

    - Emergency gas shutdown equipment shall be provided by the manufacturer as a complete system.

    - Install emergency gas shutdown equipment including emergency shunt switches, and gas solenoid valves as shown on Contract Drawings, and as recommended by manufacturer of equipment, and as required by authorities having jurisdiction.

    - Install conduit and wiring from device, gas valve, contactor and remote panic buttons as recommended by manufacturer of equipment.

  - SEQUENCE OF OPERATION

    - Remote Panic Button input shall activate high alarm protocol.

    - The panic button shall provide a manual re-set function that will re-energize the gas valve allowing the gas supply and the appliances to resume.

  - COMMISSIONING

    - After installation, test equipment to demonstrate operation of functions described above under sequence of operation by manufactures certified service technician.

  - WARRANTY.

    - Limited Warranty

      - American Gas Safety, LLC. warrants to the original purchaser and/or ultimate customer ("Purchaser") of AGS products ("Product") that if any part thereof proves to be defective in material or workmanship within thirty six (36) months, such defective part will be repaired or replaced, free of charge.

END OF SECTION